## Slide 1
Digital Twin Co-Optimization of District Energy Networks and Flexible AI Workloads
ENERGY 291 · Stanford University · June 9, 2026 Victoria Dinov · Jasmine Blust · Morgan Wyatt Stanford Central Energy Facility & SRCF Digital Twin
INTRODUCTION
The explosive growth of generative AI has introduced unprecedented challenges for grid operators. Historically treated as static, inflexible loads, modern data centers possess an unexploited opportunity to act as dynamic demand-side agents.
The asynchronous nature of deep learning training provides inherent flexibility to shift delay-tolerant workloads to optimized periods—responding to grid stress, price volatility, and marginal carbon signals.
By treating AI compute as a Virtual Power Plant (VPP), operators can modulate real-time power consumption, transforming data center demand from an infrastructure liability into a grid-stabilizing asset.
Stanford’s Central Energy Facility (CEF) provides a unique co-location opportunity—integrating large-scale thermal energy storage (TES) with AI compute scheduling across the Stanford Research Computing Facility (SRCF).
DATA SOURCES
Full year of hourly operational data (May 2025–May 2026): electrical load, heating/cooling demand, TES tank states, HRC capacity limits (2,500 tons), COP parameters, and CAISO Day-Ahead Market prices.
Levelized Long-Run Marginal Emission Rate (LRMER) for California—capturing Duck Curve dynamics of CAISO grid carbon intensity (kgCO₂/MWh).
8,760-hour compute arrival trace synthesized from sub-hourly GPU/CPU utilization metadata. Raw 36,500 MWh annual payload scaled to Stanford’s 6 MW capacity envelope.
METHODS: MILP FORMULATION
• At: Local AI compute executed (MW), max 6.0 MW
• Qt: Queue backlog (MWh), max 500 MWh (5-day buffer)
• Ot: Emergency cloud outsource (MWh)
• Ut ∈ {0,1}: HRC on/off commitment
• Schwt, Shwt: TES chilled/hot water states
RESULTS
The MPC framework was benchmarked against an uncoordinated baseline—a zero-queue-delay scenario forcing all excess compute to AWS Spot at $1,200/MWh. Results demonstrate profound improvements across cost, carbon, and grid flexibility.
SENSITIVITY ANALYSIS
Robustness evaluated across SLA delay tolerances (0–120 hrs) and AWS cloud spot pricing ($600–$2,400/MWh).
ANNUAL COST & CARBON SAVINGS
• Baseline total cost: $15,177,824 — driven largely by $7.2M+ in forced AWS Spot outsourcing
• MPC total cost: $7,964,237 — cloud outsourcing completely eliminated via 500 MWh virtual queue
PEAK SHAVING & DIURNAL SHIFTING
The Load Duration Curve (Fig. 1) reveals the MPC’s effect is not classical peak shaving but a rightward compression: consumption is consolidated into deliberate mid-range hours (≈9.5 MW sustained from hours 3,500–6,500).
The 24-hour average dispatch profile shows the MPC actively suppressing grid draw during the expensive Duck Curve “neck” (hours 16–21) and shifting processing into overnight and solar-dominant midday windows—simultaneously arbitraging cost and carbon.
DISCUSSION
• Thermodynamic co-optimization of district thermal storage with AI compute queuing via rolling MPC
• Quantified financial and carbon value of SLA delay tolerance in research computing
• Scalable blueprint for large-load grid interconnections co-located with zero-carbon thermal systems
• Demonstrated multi-objective trade-off: carbon benefit outweighs marginal off-peak cost premium
FUTURE WORK
• Stochastic MPC with renewable forecast uncertainty
• Demand response contracts and grid ancillary service markets
• Cooperative game theory framework for multi-campus VPP coalitions
• Real-time implementation with SRCF job scheduler integration
• CVaR-based risk-averse formulation for carbon price volatility
REFERENCES
[1] Stanford SESI, Central Energy Facility, 2026.
[2] Stanford HAI, AI Index Report, 2025.
[3] SLAC National Accelerator Laboratory, Computing Infrastructure, 2022.
[4] NLR, HPC Data Center PUE, 2026.
[5] Gagnon, Cambium 2024 Data, NREL, doi:10.7799/2560791.
[6] Alibaba Systems Architecture Lab, Cluster-Trace-GPU-v2020, 2020.
[7] Amazon Web Services, EC2 Spot Instances Pricing, 2026.